## Slide 1: LOGO! Communication Modules Remote control and monitoring with LOGO! Technical slides
siemens.com/logo
Unrestricted © Siemens 2020
February 2020

## Slide 2: Agenda
Technology / portfolio
2
Benefits
3
Use Cases
4
Technical Details
5
Order information and logistic
6
Target customers
7
Support
8
Positioning
1

## Slide 3: LOGO! Modular PLC – positioning
  LOGO! – for simple automation tasks
  LOGO! – mainly for stand alone applications
  LOGO! – offers ready to use function blocks for various applications, other than in controllers where these functions must be programmed explicitly
  LOGO! – fits into the standard cabinets for building applications and is certified for domestic areas (limit Class B Group 1)
Application complexity
Resource power I/O capacity, program size, instruction speed, communication capabilities …
The modular controller for system solutions in mid-range to high-end discrete automation
Micro
Basic
Nano
Advanced
The modular compact controller for solutions in basic discrete and standalone automation
Logic module for switching and controlling solutions in small-scale automation projects
SIMATIC S7-1500
SIMATIC S7-1200
LOGO!

## Slide 4: LOGO! – The ideal solution in between auxiliary relays and controllers
  LOGO! closes the gap between relays, auxiliary contactors, timers and the world of controllers
  LOGO! means connecting functions logically by mouse-click instead of wiring
  LOGO! is the perfect introduction into the world of automation just below the world of controllers
Time relay
LOGO! Logic module
SIMATIC S7-1200 PLC
Auxiliary contact
Functionality
Price

## Slide 5: Agenda
Positioning
1
Benefits
3
Use Cases
4
Technical Details
5
Order information and logistic
6
Target customers
7
Support
8
Technology / portfolio
2

## Slide 6: LOGO! product overview
4 basic modules with and without display, all with Ethernet interface
8 inputs 4 outputs, expandable up to max.: 24 DI, 20 DO, 8AI und 8 AO
Modules for different Voltages
  12/24 V DC, relays-outputs 10A, 4 inputs as 0-10V AI useable
  24 V DC, transistor-outputs, 4 inputs as 0-10V AI useable
  24 V AC DC, relays-outputs 10 A
  115 -240 V ACDC, relays-outputs 10A
LOGO! expansion modules
  Digital: DM8 with 4 DI/4 DO; DM 16 with 8 DI/8 DO (diverse voltages)
  Analog: AM2 with 2 analog inputs 0-10V,0/4-20mA AM2 RTD with2 analog inputs for PT 100 / PT1000 AM2 AQ with 2 analog outputs 0-10V,0/4-20mA
LOGO! TDE
  6 lines, each 20 characters
  3 switchable background colors to highlight different kinds of messages
  2 Ethernet-Interfaces
  4 function keys

## Slide 7: LOGO! additional components
LOGO! CMR 2020 / 2040 communication module for GSM und GPS
Remote access on LOGO! 8 via SMS (sending/receiving)
Symbolic names (Alias) for SMS
Send e-mails
Remote programming via open VPN
Position determination via GPS, e.g. for container tracking
Time synchronization
Programming via web browser
+
LOGO! CSM
Switch with 4 ports
One port at the front for direct access inside control cabinets
+
LOGO! Power
4 versions for 24 V 0,6 A; 1,3 A; 2,5 A and 4 A
3 versions for 12 V 0,9 A; 1,9 A and 4,5 A
LOGO! CMK2000 Communication module for integration into KNX building bus systems
Communication between LOGO! and KNX actuators/ sensors
Programming via KNX Software ETS
+
+

## Slide 8: LOGO! highlights This is LOGO!
Display
6 lines each 16 characters
3 background colors
LOGO! text display
6 lines each 20 characters
3 background colors
2 Ethernet connections
4 function keys
Micro SD-Card slot
Easy uploading and downloading of programs to the LOGO!
Usable for data-logging
Know-How protection
All LOGO! devices include communication via Ethernet
LOGO!  LOGO!
LOGO!  HMI
LOGO!  S7-Controller
LOGO!  Modbus TCP/IP
LOGO! => PC (Access Tool)
Time synchronization
LOGO! Soft Comfort V8.2
Single and network mode
Programming Communication via drag & drop
Programming of Modbus communication and time synchronization
Integrated webserver
Design websites with own images and icons – without HTML
No HTML knowledge necessary
Or view like message text and TDE
View like LOGO! or LOGO! TDE with use of function keys
Temperature range
-20 °C to 55 °C
+
+
+
+
+

## Slide 9: LOGO! CMR highlights
Configuration via
Web Interface
Position detection using
GPS-signal
Time synchronization of
LOGO! using
  GPS
  GRPS (NTP)
  Mobile radio network provider
Stand alone functionality
with 2 DI and 2 DO
Monitoring, alerting and control of distributed systems via SMS and / or e-mail
Mounting Options:
  35mm DIN rail (DIN EN 50022)
  Wall mounting
Simple diagnosis using LED
  Supply voltage
  LAN status
  Signal strength (mobile wireless)
  Status LED for DI and DO
Use of an intuitive, easy-to-remember SMS Syntax
Remote Access via OpenVPN and HTTP to LOGO! CMR und LOGO! Basic Module
+
+
+
+
+
+
+
+
+

## Slide 10: LOGO! CMR Functions
Position detection of the LOGO! CMR per GPS signal
  Forward of the position data in the LOGO! Logic Module and query via SMS
Time-of-day synchronization
  The time of the LOGO! basic unit can be set by transferring the received time from LOGO! CMR
  by UTC-Time of an accessible NTP-Server
  Time of the GPS-Signal or the cellular network providers
Remote Communication via mobile wireless networks (CMR2020 GSM/GPRS; CMR2040 LTE, UMTS)
  Reading/writing of data from/to the LOGO! basic units using intuitive* SMS
  Event-driven alerting using SMS and /or e-mail*
  Simple switch processes via digital integrated IOs: Reading the inputs and switching of the outputs of the LOGO! CMR
Secure Remote Access* via mobile wireless networks to
  LOGO! CMR ( Web Interface via OpenVPN/HTTP)
LOGO! Basic Module via OpenVPN and http with Web server or LOGO! App for Up-/Download of the LOGO! SoftComfort programs).
Remote control, monitoring and programming for LOGO!

## Slide 11: LOGO! CMR Further functions with firmware V2.0
Further Improvements:
  Test SMS / e-mail for IBS
  Monitoring of GPS-Position on Web Interface
  Further Diagnostic Informations (Counter for SMS/e-mail successful/lost send/received)
  Timesynchronization out of actualisation interval
  Acknowledgement of incoming SMS
  Default Router for LAN-Interface
Extensions of the SMS-Syntax
  Write/Read single Bits
  Alias SMS
  Using of configured signal names also in SMS-Syntax
  SMS password optional
Optional using of a simple Web Interface Password
Using a DynDNS-Dienst, to reach the LOGO! CMR via Host-Name, e.g. "myName.dyndns.org„ (DynDNS or noip)
Further functions with firmware V2.0

## Slide 12: LOGO! CSM Highlights
Mounting Options:
  35mm DIN rail (DIN EN 50022)
  Wall mounting
+
LOGO! 8 Design
  Switch for junction box with one RJ45-Port on the front
  Ideal for use with LOGO!
  Stand-alone application
+
Simple diagnosis using LED
  Supply voltage
  Link status and transfer of data per port
+
Terminal block for
  Power supply
+
Unmanaged Industrial Ethernet Switch
  4x RJ45 Ports
  10/100 Mbit/s
  Auto negotiation and auto crossing
+
+

## Slide 13: LOGO! CSM unmanaged Compact Switch Module Functional overview
  Industrial Ethernet Switch in the form factor of LOGO! with 4 electrical RJ45 ports 10/100 Mbit/s with auto crossing and auto negotiation
  Low-cost setup of small machine networks
  Fast commissioning without configuration
  Simple local diagnostics via LEDs
Ideal for Networking of small systems with LOGO! or SIMATIC S7
Notes: Notizen 13

## Slide 14: Agenda
Positioning
1
Technology / portfolio
2
Use Cases
4
Technical Details
5
Order information and logistic
6
Target customers
7
Support
8
Benefits
3

## Slide 15: LOGO! Benefits
Features/ functions |  | Benefit
8 basic modules with Ethernet and integrated Webserver |  | Communication with all S7-Systems Remote control and monitoring Insert your own pictures and symbols
Extended temperature range for basic and expansion modules -20° to +55°C |  | Cost efficient solution for use at low temperatures
NTP server/client for date and time synchronization |  | All LOGO! devices in a network show the same time
Integrated Modbus TCP/IP protocol as client and server |  | Simple communication to third parts devices via Ethernet
LOGO! Access Tool as excel add-in to read and archive process data LOGO! Web editor |  | Process values can be analyzed, archived and visualized in Excel while the process is running

## Slide 16: LOGO! CMR Benefits
Features / Functions |  | Benefit
Read/write data/variables from/to LOGO! 8 basic unit using SMS and e-mail |  | Low-cost and easy-to-use alarm messaging system
Secure remote access to LOGO! CMR and LOGO! BM |  | Low-cost remote access via SMS for operating and controlling the LOGO! logic module
Time-of-day synchronization via NTP server, GPS signal or mobile network provider and forwarding to LOGO! basic unit |  | Simple realization of time-controlled control tasks with Logikmodul LOGO!
Position detection of the LOGO! CMR per GPS signal and query option per SMS |  | Position detection e.g. Container in logistics applications

## Slide 17: LOGO! CSM12/24 Benefits
Feature / Function |  | Benefit
For connecting a LOGO! and up to three other nodes to an Industrial Ethernet network |  | Implementation of low-cost Industrial Ethernet networks for connecting LOGO! basic units
1 RJ45 Port at front side |  | Freely accessible Ethernet port on front side for direct diagnostics access when installing in a cabinet
Design of LOGO! |  | Industrial design of the new LOGO! generation Space-saving installation for connection to LOGO! 8 optimized

## Slide 18: Agenda
Positioning
1
Technology / portfolio
2
Benefits
3
Technical Details
5
Order information and logistic
6
Target customers
7
Support
8
Use Cases
4

## Slide 19: Networking with LOGO! CSM12/24
Networking with LOGO! CSM12/24
With the LOGO! CSM12/24 in the form factor of LOGO! 8, up to 4 Ethernet devices with 10/100 Mbit/s can be connected. As an unmanaged Ethernet Switch with 4 electrical RJ45 ports 10/100 Mbit/s with auto crossing and auto negotiation, the CSM requires no commissioning
Solution
Benefit
Networking of small systems with LOGO! or SIMATIC
Low-cost setup of small machine networks
Fast commissioning without configuration
Simple local diagnostics via LEDs
Task

## Slide 20: Monitoring, alerting and control of distributed systems using SMS, e.g. monitoring of a water tank with LOGO! CMR
Monitoring, Alerting and Control of Distributed Systems using SMS, e.g. Level Monitoring of a Water Tank with LOGO! CMR
Solution
Benefit
Task
Remote monitoring of the level of a water tank, and control via an outlet valve
The LOGO! CMR monitors the process image of the defined signals of the LOGO! basic unit.
If a defined event occurs, such as the setting of an input, a text message is sent to a defined group of mobile telephone numbers.
Conversely, the CMR can receive a text message and transfer appropriate values to the LOGO! which can then respond according to these values.
Low-cost solution for simple remote stations based on the LOGO! logic module
Note: Example: Syntax of received SMS Password;LOGO=VM125,1,BYTE

## Slide 21: Time-of-day synchronization using LOGO! CMR by means of NTP, Mobile Network Provider or GPS
Time-of-day synchronization using LOGO! CMR by means of NTP, Mobile Network Provider or GPS
Solution
Benefit
Task
The CMR enables automatic time synchronization of the LOGO! using different procedures
Forwarding of the time-of-day of the mobile network provider
LOGO! CMR calculates the time-of-day for the NTP server to be defined on the Internet
LOGO! CMR receives the UTC time by satellite via GPS
Use of the LOGO! as the control unit for church tower clocks or school clocks, e.g. sending signals for break time, or controlling church bells. Regular time synchronization is required in this case.
Easily parameterized solution for synchronizing the LOGO! with a local time-of-day (including summer/winter time adjustment
Note: There is no mobile wireless communication needed for Time-of-day synchronization

## Slide 22: LOGO! CMR calculation of position data by means of GPS
LOGO! CMR Calculation of Position Data by means of GPS
Solution
Benefit
Task
The LOGO! CMR calculates the position from the GPS signal received via GPS antenna from the satellite and triggers an appropriate configured action. The determined position e.g. will be sent per SMS by the LOGO! CMR or will be sent to the LOGO! BM. In the LOGO! BM the GPS-Signal can be logged and, if necessary be queried via the LOGO! CMR.
Continuous recording of the position data of a container, for example, and querying of the data if required.
Low-cost solution for position detection by GPS signal via query option using text messages
Note: Example: Syntax of received SMS to get the GPS-position: GPSPOSITION? Response SMS: GPS-Position: 49:0:50.4 N 8:24:15.48 E Alt 0350

## Slide 23: LOGO! CMR Symbolic addressing / Alias SMS
Symbolic addressing / Alias SMS
Example-SMS for request the level:
Stufe1: LOGO?VM125,Word
Stufe2 - symbolisch: LOGO?Level1 Stufe2 - Alias: Level1
Example-SMS to set the max. level:
Stufe 1: Hugo;LOGO=VM127,40,WORD
Stufe 2 – symbolisch: Hugo;LOGO=levellmax,40
Stufe 2 – Alias: levelmax
The LOGO! CMR monitors the process image of the defined signals of the LOGO! basic module
If a defined event (e.g. setting an input), a SMS to a defined group of mobile phone numbers (user) is sent
The level could also be requested by a defined user.
The user should be able to send the permitted level value via SMS to CMR. This transfer the value to the LOGO! BM.
For SMS-Syntax, the user can use the symbolic addressing or the Alias SMS
Task
Remote Monitoring and Control of the level of a water tank
Solution
Simple usability – the user must not longer work with complicated SMS-Syntax. He can easily put together useable commands
Benefit

## Slide 24: Secure remote access to LOGO! CMR and LOGO! BM
Secure Remote Access to LOGO! CMR and LOGO! BM
From a remote station (Smartphone/ Tablet), you can call the Web Interface of the LOGO! CMR via OpenVPN and http to change settings.
At the same time you can call the Web Interface of the LOGO! BM which is connected to the LOGO! CMR via OpenVPN.
It is also possible to download a LSC-Project via this OpenVPN Tunnel to the LOGO! BM
You can also start the LOGO! App via this tunnel.
Task
LOGO! CMR and LOGO! BM should be configurable via Smartphones / Tablet.
Solution
Benefit
Reduction of travel costs, allowing remote access to configuration and diagnostics over the mobile wireless network.

## Slide 25: Examples of stand-alone applications for LOGO! CMR
Examples of stand-alone applications for LOGO! CMR
Solution
Benefit
Task
The LOGO CMR enables direct connection of actuators, e.g. for light control via 2 integral digital outputs with control via SMS.
Sensors can be connected via the additional 2 integral digital inputs, e.g. for monitoring the current status, and likewise read out by means of SMS text messages.
Remote control of switching operations, e.g. for light control in a poorly accessible hall.
Low-cost solution for remote control of digital sensors and actuators.
Note: Example: Syntax of a received SMS to set an internal digital Output: Password;OUTPUT=O1,1

## Slide 26: Agenda
Positioning
1
Technology / portfolio
2
Benefits
3
Use Cases
4
Order information and logistic
6
Target customers
7
Support
8
Technical Details
5

## Slide 27: LOGO! CMR Design
SMA socket for mobile wireless antenna
SMA socket for GPS antenna
Card slot behind cover for:
  Micro SD cards
  SIM cards
Connection to LOGO! 8
  Industrial Ethernet RJ45
  100 Mbit/s with Autosensing and auto crossover function
Recessed SET button for resetting to factory setting
Terminal sockets for power supply
Status LEDs for inputs and outputs
Diagnostics LEDs for
Supply voltage
Link status on the LAN
Reception’s quality of the mobile wireless signal
Fault
Terminal sockets for digital input and output signals
Mounting options:
  Mounting rails (35 mm according to DIN EN 50022)
  Wall mounting

## Slide 28: LOGO! CMR Technical data
 | LOGO! CMR2020 | LOGO! CMR2040
Housing | 4TE (72 mm) | 
Programming interface | Industrial Ethernet (RJ45) or mobile wireless | 
Memory card for mobile wireless | SIM cards or Micro SD card | 
Connection for mobile wireless antenna | SMA socket (50 ohms) | 
Supported mobile wireless networks/services | GSM / GPRS | GSM / LTE
Connection for GPS antenna | SMA socket (50 ohms) | 
Inputs/outputs (DI / DO) | 2 / 2 (on terminal block) | 
External power supply | 24 V DC (on terminal block) | 
Industrial Ethernet | 1 x RJ45 (10/100 Mbit/s) | 
Temperature range in operation | -20°C … +70°C | 
Degree of protection | IP20 | 
Mounting method | Standard mounting rail or wall mounting | 

## Slide 29: LOGO! CMR Key data / Quantities
 | LOGO! CMR
Default Login / Password | admin/ admin
Default IP-Address | 192.168.0.3
Subnet mask | 255.255.255.0
Maximum definable user/ phone numbers | 20
Maximum definable user groups | 10
Maximum definable signals, which can be monitored | 32
Maximum definable events, which can be occur | 32
Maximum definable actions, which can be triggered | 32
Maximum definable associations between events and actions | 32

## Slide 30: LOGO! CMR function: SMS receive Syntax overview of the possible SMS, which can be received
Read information from CMR | Example Syntax SMS command
Read diagnostic data from CMR | DIAG?
Read GPS-Position from CMR | GPSPOSITION?
Read process image | MONITOR?
Read status of the LOGO! BM | STATUS?
Read current value | LOGO?VM125,WORD
Influence data in CMR/LOGO! BM | Example Syntax SMS command
Change Status of LOGO! BM | Password;STATUS=RUN
Write current value | Password;LOGO=VM125,1,WORD
Set Digital Output of CMR | Password;OUTPUT=O1,1
Change phone number of one user | Password;CHANGEUSER=„Joe“;“01721234567“
Configure address of NTP-Server | Password;NTPSERVER= "217.13.75.19"
Request to cellular network provider via service code | Password;SERVICECODE=„*100#“

## Slide 31: Commissioning LOGO! CMR First steps
What to do ?
Hardware installation
Web Interface
See also included product information and manual

## Slide 32: Configuration with web based management Start page

## Slide 33: Configuration with web based management Mobile wireless settings
Password SIM-Card
Password Received SMS

## Slide 34: Configuration with web based management Activate GPS
Activate GPS

## Slide 35: Configuration with web based management Time-of-day synchronization
For GPS only
Activate “drop down menu „Activate GPS“ at register ”System”
Options Update Interval:
1 hour
12 hours
1 day
Forward to LOGO! BM
For NTP only,
Input address of NTP Server
Activate drop down menu “Activate data connection via the mobile wireless network” at register “Mobile wireless settings”
Options:
NTP
GPS
Cellular network provider

## Slide 36: Configuration with web based management Signal monitoring

## Slide 37: Configuration with web based management Example
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff (SMS message).
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".
Activate Connection to LOGO! BM

## Slide 38: Configuration with web based management Create user
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff (SMS message).
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".

## Slide 39: Configuration with web based management Create user group
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff (SMS message).
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".

## Slide 40: Configuration with web based management Monitoring-/message configuration in 5 steps
Requirement for / Assignments
Message texts
Define possible SMS message texts
4. Define possible actions
Possible actions:
Send SMS
Set CMR output
Start / Stop Basismodul
Actions
Signal definitions
2. Define signals, that the CMR can use
Events
5. Which event activates which action?
3. Define activation events
Possible events:
Basismodul-variable change
CMR-input change
Timer expiration

## Slide 41: Monitoring-/message configuration 1. Define message text
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff in form of an SMS message.
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".

## Slide 42: Monitoring-/message configuration 2. Define signal
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff in form of an SMS message.
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".

## Slide 43: Monitoring-/message configuration 3. Define events
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff in form of an SMS message.
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1“.

## Slide 44: Monitoring-/message configuration 4. Define action e.g. SMS
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff in form of an SMS or e-mail message.
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".
Information of the action e.g. SMS or e-mail senden and Selection „Action“ to LOGO! CMR or LOGO! BM
Depending on which action was selected the other fields will appear/ disappear, e.g. for the specification of the message text

## Slide 45: Monitoring-/message configuration 5. Define assignments: event to action
  A water tank holds 100 liters. If the volume of 100 liters is exceeded, an alarm message will be sent to the maintenance staff in form of an SMS message.
  The maintenance staff consists of two employees, employee "User-1" and employee "User-2" whose phone numbers are known. The employees are organized in a group called „Maintenance Staff“
  A fill level sensor is connected to input no. 1 of the LOGO! BM: If the measurement indicates that the amount of liquid has been exceeded (> 100 liters in the tank), the fill level sensor sets digital input no. 1 to "1".
Then (Action e.g. send messagetext)
If (Event due to signal)

## Slide 46: Configuration via web based management Alias-SMS – <WAN> <SMS – Alias>
SMS-Syntax“ – Input of the LOGO! CMR interpretable SMS-Syntax e.g. Passwort;LOGO=VM125,1,WORD
„SMS-Alias“ – Input of an intuitive command, this will be used in this syntax on the mobile phone
e.g. LightOn

## Slide 47: Configuration via web based management Symbolic name in SMS-syntax
Symbolic value name
Change/ read data at CMR/LOGO! BM | Example Syntax SMS-Befehl | New with symbolic tag name | Example for Alias SMS
Write current value | Password;LOGO=VM125,1,Byte | Password;LOGO=Light,1 | LightOn
Set DI Output CMR | Password;OUTPUT=O1,0 | Password;OUTPUT=CMR_Q1, 0 | Gate1 close
Read current value | LOGO?VM125,WORD | LOGO?Quantity_Target | Level1

## Slide 48: Configuration via web based management Symbolic name in SMS-syntax
Symbolic name / constants
Change read/ write CMR/LOGO! BM | Example Syntax SMS-Befehl | New with symbolic tagname | Example for SMS-Alias
Write current value | Password;LOGO=VM125,dynWert,BYTE | Password;LOGO=VM125, Quantity_Normal, Byte Quantity_Normal is defined as a signal in the signal definition and is as supplied by a value of the LOGO! BM | Temperatur change
Set Digital Output CMR | Passwort;OUTPUT=O1,dynWert | Password;OUTPUT=O1, OFF | Gate1 close

## Slide 49: LOGO! CMR diagnostics
Diagnostic buffer
…
Wireless cell

## Slide 50: Remote access connection to LOGO! BM Security settings OpenVPN
If the Pre-shared Key should be generated at the partner (OpenVPN-Client), the file could be imported here.
If the Pre-shared Key should be generated at CMR, it could be started via this Button.

## Slide 51: LOGO! CSM Design
LOGO! Design
Switch for junction box (4TE) with one Ethernet Port on the front
Terminals for power supply
Diagnostics-LEDs for
  supply voltage
  Link status and data transfer per port
Mounting Options:
  Mounting rails (35mm according to DIN EN 50022)
  Wall Mounting
Industrial Ethernet port e.g. for configuration and diagnostics, also accessible in the junction box without opening the cover 1 Port RJ45
  100 Mbit/s with auto sensing and auto crossover functionality
Industrial Ethernet connection
  3 Ports RJ45
  100 Mbit/s with auto sensing and auto crossover functionality

## Slide 52: Agenda
Positioning
1
Technology / portfolio
2
Benefits
3
Use Cases
4
Technical Details
5
Target customers
7
Support
8
Order information and logistic
6

## Slide 53: LOGO! Ordering data
Simply brilliant for small automation tasks
Logic module LOGO!
You can find the current version of the brochure on the Internet
Click here:

## Slide 54: LOGO! Communication modules Ordering data
Device | MLFB | Description
LOGO! CMR2020 | 6GK7142-7BX00-0AX0 | LOGO! CMR2020 communication module for connection LOGO! 8 to GSM/GPRS network; 1 RJ45 port for Ind. Ethernet connection to LOGO! 8; 2xDI; 2xDQ; Write/read access to LOGO! tags; Text message sending/ receipt; E-mail sending; Position detection GPS; Time synchronization/ forwarding with real-time clock; Configuration/diagnostics via web interface; Remote access via OpenVPN/HTTPs, DynDNS; Observe national approval! Manual available as a download
LOGO! CMR2040 | 6GK7142-7EX00-0AX0 | LOGO! CMR2040 communication module for connection LOGO! 8 to LTE network; 1 RJ45 port for Ind. Ethernet connection to LOGO! 8; 2xDI; 2xDQ; Write/read access to LOGO! tags; Text message sending/ receipt; E-mail sending; Position detection GPS; Time synchronization/ forwarding with real-time clock; Configuration/diagnostics via web interface; Remote access via OpenVPN/HTTPs, DynDNS, observe national approval! Manual available as a download
LOGO! CSM12/24 | 6GK7177-1MA20-0AA0 | LOGO! CSM12/24 Compact Switch Module connection of a LOGO! (. ..0BA7/...0BA8) and up to 3 further nodes to Ind. Ethernet with 10/100 Mbit/s Unmanaged switch, 4 RJ45 ports, 1x front port for diagnostics DC 12/24V power supply LED diagnostics, LOGO! setup

## Slide 55: LOGO! CMR Ordering data Accessories 1
Mobile Wireless Antenna: | 
ANT794-4MR (6NH9860-1AA00) ANT794-4MR mobile wireless antenna for 2G/3G/4G EU, GSM/UMTS/ LTE EU networks, Rod antenna; omnidirectional; weatherproof for indoors and outdoors; 5 m Connection cable permanently connected to the antenna; SMA connector; incl. mounting bracket, screws, screw anchor | 
ANT896-4MA (6GK5896-4MA00-0AA3) ANT896-4MA mobile wireless antenna for GSM (2G), UMTS (3G) and LTE(4G) networks; Omnidirectional Characteristic, Radially rotatable, with additional joint, Antenna gain: 2 dBi, incl. SMA connector, IP54, (-40-+85°C), Observe national approvals; for direct installation with SMA connection system scope of delivery: 1x ANT 896-4MA, compact instructions as hard copy German/English | 
ANT896-4ME (6GK5896-4ME00-0AA0) ANT896-4ME mobile wireless antenna for GSM (2G), UMTS (3G) and LTE(4G) Networks, Omnidirectional Characteristic, incl. N-female connector: 3 dBi; IP66 (-40-+70°C), Observe national approvals; mounting on control cabinet; scope of delivery: 1x ANT 896-4ME, compact instructions as hard copy English/German | 
GPS Antenna: | 
ANT895-6ML (6GK5895-6ML00-0AA0) ANT895-6ML GPS antenna Antenna with integrated signal amplifier incl. 0.3 m connection cable and N-female connector; 3 dBi IP67 (-40...+85 °C) Mounting with magnet or Screw mounting Observe national approvals; compact instructions as hard copy English/German; scope of delivery: 1x ANT 895-6ML | 

## Slide 56: LOGO! CMR Ordering data Accessories (2)
Connecting Cable:
SIMATIC NET N-CONNECT/SMA MALE/MALE FLEXIBLE CONNECTION CABLE pre-assembled suitable for 0..6 GHz, IP68 Lengths: 6XV1875-5LE30 0,3m 6XV1875-5LH10 1m 6XV1875-5LH20 2m 6XV1875-5LH50 5m
SIMATIC NET N-CONNECT MALE/MALE FLEXIBLE CONNECTION CABLE pre-assembled; suitable for 0..6 GHz, IP68 Lengths: 6XV1875-5AH10 1m 6XV1875-5AH20 2m 6XV1875-5AH50 5m 6XV1875-5AN10 10m
Control Panel Feed Through:
PANEL FEEDTHROUGH (6GK5798-2PP00-2AA6) N-Connect Female/female Panel feedthrough, cabinet bushing, 2.4 GHz and 5 GHz for Wall thickness max. 4.5 mm
Lightning protector LP 798-1N (6GK5798-2LP00-2AA6) Lightning protection element with N/N female/female connection, IP66/68 (-40 °C...+85 °c), 0...6 ghz, with gas discharge technology for scalance w and m antennas, compact instructions as hard copy german/english

## Slide 57: Connecting the antennas to the LOGO! CMR Configuration with GPS und cellular network
LOGO! CMR with Remote Antennas
LOGO! CMR: directly connected Cellular Network Antennas

## Slide 58: Connecting the antennas to the LOGO! CMR in the control cabinet – configuration with GPS und cellular network
LOGO! CMR with Panel Feed Through
LOGO! CMR with Panel Feed Through incl. Lightning Protect

## Slide 59: Agenda
Positioning
1
Technology / portfolio
2
Benefits
3
Use Cases
4
Technical Details
5
Order information and logistic
6
Support
8
Target customers
7

## Slide 60: Typical application areas
  Simple remote monitoring and remote control tasks (also in domestic applications such as heating control, window control, garden watering)
  Building automation including building equipment for HVAC and pump control, for example
  Irrigation, automatic feeders in agriculture
  Remote control and monitoring of low-end machine control (usually discrete logic)
  Remote control and monitoring of level, pressure, temperature and flow, and valve control in the water/wastewater industry
  Position monitoring in the logistics field (e.g. vehicles, refrigerated transporters, containers)
  Basic energy monitoring

## Slide 61: Agenda
Positioning
1
Technology / portfolio
2
Benefits
3
Use Cases
4
Technical Details
5
Order information and logistic
6
Target customers
7
Support
8

## Slide 62: Further information
  Movie about LOGO!
  Brochure LOGO!
  Further information on the logic module LOGO! unter:
  siemens.com/logo

## Slide 63: Thank you for your attention!
siemens.com/logo
Subject to changes and errors. The information given in this document only contains general descriptions and/or performance features which may not always specifically reflect those described, or which may undergo modification in the course of further development of the products. The requested performance features are binding only when they are expressly agreed upon in the concluded contract.
All product designations, product names, etc. may contain trademarks or other rights of Siemens AG, its affiliated companies or third parties. Their unauthorized use may infringe the rights of the respective owner

## Slide 64: Disclaimer
Subject to changes and errors. The information given in this document only contains general descriptions and/or performance features which may not always specifically reflect those described, or which may undergo modification in the course of further development of the products. The requested performance features are binding only when they are expressly agreed upon in the concluded contract.
All product designations, product names, etc. may contain trademarks or other rights of Siemens AG, its affiliated companies or third parties. Their unauthorized use may infringe the rights of the respective owner.

## Slide 65: Security information
      Siemens provides products and solutions with industrial security functions that support the secure operation of plants, systems, machines and networks.
      In order to protect plants, systems, machines and networks against cyber threats, it is necessary to implement – and continuously maintain – a holistic, state-of-the-art industrial security concept. Siemens’ products and solutions constitute one element of such a concept.
      Customers are responsible for preventing unauthorized access to their plants, systems, machines and networks. Such systems, machines and components should only be connected to an enterprise network or the internet if and to the extent such a connection is necessary and only when appropriate security measures (e.g. firewalls and/or network segmentation) are in place.
      For additional information on industrial security measures that may be implemented, please visit https://www.siemens.com/industrialsecurity.
      Siemens’ products and solutions undergo continuous development to make them more secure. Siemens strongly recommends that product updates are applied as soon as they are available and that the latest product versions are used. Use of product versions that are no longer supported, and failure to apply the latest updates may increase customer’s exposure to cyber threats.
      To stay informed about product updates, subscribe to the Siemens Industrial Security RSS Feed under https://www.siemens.com/industrialsecurity.